## Note
Legend for the data points
Min. value | Smallest possible value
Max. value | Largest possible value
TypeName | Indicates whether a data point is unsigned (U) or signed (S). The length in bit of the data point is also given. (Example: U8, S16, S32, etc.) The LIST data point can be read as U16 or S16! The content of the LIST DP, which is represented by a number, indicates which field “Text 0” to “Text 31” of the data point list means what and what text it represents.
Steps | Indicates the number of valid steps when adjusting values. (Example: 5 -> value may only take on 0, 5, 10, etc.)
Combined data points
If a data point of the Hoval CAN bus is longer than 2 bytes (U32, S32, S64), the data point is distributed to 2 or 4 Modbus data points. These are marked with a
The value is calculated as follows: low byte value + (high byte value x 65536)
If a value of 1 is sent to the high byte and a value of 34 is sent to the low byte, then you will get 34 + (1 x 65536) = 65570 kWh as the counter value

## Example 1
Heating
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
1478 | Operation choice – Heat. circ. 1 | LIST | 1 |  |  | 0 = Standby 1 = Week 1 2 = Week 2 4 = Constant 5 = Eco mode 7 = Manual operating mode heating 8 = Manual operating mode cooling
1481 | Normal room temp. – Heat. circ. 1 | S16 | 5 | 100 | 300
1479 | Operation choice – Heat. circ. 2 | LIST | 1 |  |  | 0 = Standby 1 = Week 1 2 = Week 2 4 = Constant 5 = Eco mode 7 = Manual operating mode heating 8 = Manual operating mode cooling
1483 | Normal room temp. – Heat. circ. 2 | S16 | 5 | 100 | 300
1480 | Operation choice – Heat. circ. 3 | LIST | 1 |  |  | 0 = Standby 1 = Week 1 2 = Week 2 4 = Constant 5 = Eco mode 7 = Manual operating mode heating 8 = Manual operating mode cooling
1485 | Normal room temp. – Heat. circ. 3 | S16 | 5 | 100 | 300
Hot water
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
1496 | Hot water operation choice | LIST | 1 |  |  | 0 = Standby 1 = Week 1 2 = Week 2 4 = Constant – normal mode 6 = Constant – eco mode
1497 | Normal hot water temp. | S16 | 10 | 100 | 700

## Example 2
Heating
Register Address | DatapointName | Type | Steps | Min. value | Max. value
1490 | Flow setpoint heating – Heat. circ. 1* | S16 | 10 | 100 | 1100
1491 | Flow setpoint heating – Heat. circ. 2* | S16 | 10 | 100 | 1100
1492 | Flow setpoint heating – Heat. circ. 3* | S16 | 10 | 100 | 1100
Cooling
Register Address | DatapointName | Type | Steps | Min. value | Max. value
23754 | Flow setpoint cooling – Heat. circ. 1* | S16 | 10 | 0 | 300
23755 | Flow setpoint cooling – Heat. circ. 2* | S16 | 10 | 0 | 300
23756 | Flow setpoint cooling – Heat. circ. 3* | S16 | 10 | 0 | 300
Hot water
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
1496 | Hot water operation choice | LIST | 1 |  |  | 0 = Standby 1 = Week 1 2 = Week 2 4 = Constant – normal mode 6 = Constant – eco mode
1497 | Normal hot water temp. | S16 | 10 | 100 | 700

## Example 3
Heat generator
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
1561 | Heat generator operation choice | LIST |  |  |  | 0 = Heat generator off 1 = Automatic operation 4 = Manual heating operation 5 = Manual cooling operation 8 = Manual DHW operation
1562 | Manual mode set temperature | S16 | 10 | 0 | 1100
19484 | Manual mode output setpoint | U8 | 1 | 0 | 100

## Example 4
Heat generator
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
1561 | Heat generator operation choice | LIST |  |  |  | 0 = Heat generator off 1 = Automatic operation 4 = Manual heating operation 5 = Manual cooling operation 8 = Manual DHW operation
1562 | Manual mode set temperature | S16 | 10 | 0 | 1100
19484 | Manual mode output setpoint | U8 | 1 | 0 | 100

## Example 5
HomeVent® comfort ventilation unit
Register Address | DatapointName | Type | Steps | Min. value | Max. value
23622 | Op. choice ventilation | LIST | 1 |  |  | 0 = Standby 1 = Week 1 2 = Week 2 4 = Constant 5 = Eco mode
23623 | Normal ventilation modulation | U8 | 1 | 15 | 100
23626 | Humidity set value | U8 | 1 | 30 | 65
23627 | Humidity extract air | U8 | 1 | 0 | 100

## Example 6
Heat generator information values
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
18724 | Heat generator setpoint | S16 | 1 | 0 | 1000
18725 | Heat generator actual | S16 | 1 | 0 | 1000
18726 | Modulation | U8 | 1 | 0 | 100
18737 | Operating message | U8 | 1 | 0 | 1
18722 | Status heat generator control | U8 | 1 |  |  | 0 = Switched off 1 = Heating operation 2 = Flow time heating operation 3 = Externally blocked (also for Smart Grid eco mode) 4 = Cooling operation 5 = Flow time cooling operation 15 = Alarm 16 = Fault 17 = Blocked 21 = WFmax switch-off 22 = WFsetp switch-off 26 = Bivalence deactivation 27 = Hot water charging block 28 = Minimum off time 29 = Minimum on time 32 = Supplemental operation 33 = Delay sequence H-Gen 34 = Operation overtemperature 42 = Manual operating mode heating 43 = Manual operating mode hot water 44 = Manual operating mode cooling
1507 | Operating hours heat generator_high | U32 | 1
1508 | Operating hours heat generator_low | U32 | 1
1518 | Switching cycles heat generator_high | U32 | 1
1519 | Switching cycles heat generator_low | U32 | 1
1513 | Supply actual – Heat. circ. 1 | S16 | 1 | 0 | 1000
19562 | Supply setpoint – Heat. circ. 1 | S16 | 1 | 0 | 1000
1501 | Status – Heat. circ. 1 | U8 | 1 |  |  | 0 = Switched off 1 = Normal heating operation 2 = Comfort heating operation 3 = Economy heating operation 4 = Frost operation 5 = Force acceptance (with force > +50%) 6 = Force throttling (with force < -50%) 7 = Holiday operation 8 = Party operation 9 = Normal cooling operation 10 = Comfort cooling operation 11 = Economy cooling operation 12 = Fault 13 = Manual operation 14 = Protection cooling operation 15 = Party operation cooling 16 = Drying heating-up phase 17 = Drying stationary phase 18 = Drying cooling-down phase 19 = Drying end phase 22 = Cooling operation external/constant request 23 = Heating operation external/constant request 24 = Absent heating operation 25 = Absent cooling operation 26 = Preferential operation Smart Grid heating 27 = Preferential operation Smart Grid cooling
1493 | Room setpoint – Heat. circ. 1 | S16 | 1 | 0 | 500
1514 | Supply actual – Heat. circ. 2 | S16 | 1 | 0 | 1000
19563 | Supply setpoint – Heat. circ. 2 | S16 | 1 | 0 | 1000
1502 | Status – Heat. circ. 2 | U8 | 1 |  |  | 0 = Switched off 1 = Normal heating operation 2 = Comfort heating operation 3 = Economy heating operation 4 = Frost operation 5 = Force acceptance (with force > +50%) 6 = Force throttling (with force < -50%) 7 = Holiday operation 8 = Party operation 9 = Normal cooling operation 10 = Comfort cooling operation 11 = Economy cooling operation 12 = Fault 13 = Manual operation 14 = Protection cooling operation 15 = Party operation cooling 16 = Drying heating-up phase 17 = Drying stationary phase 18 = Drying cooling-down phase 19 = Drying end phase 22 = Cooling operation external/constant request 23 = Heating operation external/constant request 26 = Preferential operation Smart Grid
1494 | Room setpoint – Heat. circ. 2 | S16 | 1 | 0 | 500
1515 | Supply actual – Heat. circ. 3 | S16 | 1 | 0 | 1000
19564 | Supply setpoint – Heat. circ. 3 | S16 | 1 | 0 | 1000
1503 | Status – Heat. circ. 3 | U8 | 1 |  |  | 0 = Switched off 1 = Normal heating operation 2 = Comfort heating operation 3 = Economy heating operation 4 = Frost operation 5 = Force acceptance (with force > +50%) 6 = Force throttling (with force < -50%) 7 = Holiday operation 8 = Party operation 9 = Normal cooling operation 10 = Comfort cooling operation 11 = Economy cooling operation 12 = Fault 13 = Manual operation 14 = Protection cooling operation 15 = Party operation cooling 16 = Drying heating-up phase 17 = Drying stationary phase 18 = Drying cooling-down phase 19 = Drying end phase 22 = Cooling operation external/constant request 23 = Heating operation external/constant request 26 = Preferential operation Smart Grid
1495 | Room setpoint – Heat. circ. 3 | S16 | 1 | 0 | 500
1499 | Hot water setpoint | S16 | 1 | 0 | 1000
1500 | Hot water actual SF | S16 | 1 | 0 | 1000
1504 | Status domestic hot water control | U8 | 1 |  |  | 0 = Switched off 1 = Normal charging operation 2 = Comfort charging operation 3 = Forced throttling (with forced E < -50%) 4 = Forced charging (with forced E > +50%) 5 = Malfunction 6 = DHW draw-off (draw-off of domestic hot water active) 7 = Warning 8 = Reduced charging operation 9 = Frost operation 12 = Preferential operation Smart Grid 13 = Forced acceptance Smart Grid
Comfort ventilation information values
Register Address | DatapointName | Type | Steps | Min. value | Max. value | Possible values
23625 | Ventilation modulation | U8 | 1 | 15 | 100
23628 | VOC extract air | U8 | 1 | 0 | 100
23629 | VOC outdoor air | U8 | 1 | 0 | 100
23630 | Air quality control | LIST | 1 | 0 | 1
23631 | Status vent. regulation | U8 | 1 |  |  | 0= OFF 1 = Normal ventilation mode 2 = VOC mode active 3 = Humidity mode active 4 = Frost protection active 5 = CoolVent active 6 = Fault status 7 = Summer humidity 8 = Switch-off stop set value
23632 | Outside air temp. | S16 | 1 | -300 | 500
23633 | Extract air temp. | S16 | 1 | 0 | 500
23634 | Fan exhaust air set | U8 | 1 | 0 | 100