## Beispiel 1
Heating
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
1478 | Heating operation choice – Heat. circ. 1 |  | 6 – Write single register | LIST | 1 | 0 | 0 | 8 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode, 7 = Manual operating mode heating, 8 = Manual operating mode cooling
1481 | Normal room temp. – Heat. circ. 1 | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 30 | E.g. 25°C
1479 | Heating operation choice – Heat. circ. 2 |  | 6 – Write single register | LIST | 1 | 0 | 0 | 8 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode, 7 = Manual operating mode heating, 8 = Manual operating mode cooling
1483 | Normal room temp. – Heat. circ. 2 | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 30 | E.g. 25°C
1480 | Heating operation choice – Heat. circ. 3 |  | 6 – Write single register | LIST | 1 | 0 | 0 | 8 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode, 7 = Manual operating mode heating, 8 = Manual operating mode cooling
1485 | Normal room temp. – Heat. circ. 3 | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 30 | E.g. 25°C
Domestic hot water
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
1496 | Domestic hot water operation choice |  | 6 – Write single register | LIST | 1 | 0 | 0 | 6 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant – normal mode, 6 = Constant – eco mode
1497 | Normal hot water temp. | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 70 | E.g. 60°C

## Beispiel 2
Heating
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
1490 | Flow setpoint heating – Heat. circ. 1* | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 110 | E.g. 30°C
1491 | Flow setpoint heating – Heat. circ. 2* | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 110 | E.g. 30°C
1492 | Flow setpoint heating – Heat. circ. 3* | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 110 | E.g. 30°C
Cooling
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
19482 | Flow setpoint cooling – Heat. circ. 1* | °C | 6 – Write single register | S16 | 0.5 | x10 | 0 | 30 | E.g. 18°C
23755 | Flow setpoint cooling – Heat. circ. 2* | °C | 6 – Write single register | S16 | 0.5 | x10 | 0 | 30 | E.g. 18°C
23756 | Flow setpoint cooling – Heat. circ. 3* | °C | 6 – Write single register | S16 | 0.5 | x10 | 0 | 30 | E.g. 18°C
Domestic hot water
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
1496 | Domestic hot water operation choice |  | 6 – Write single register | S16 | 1 | 0 | 0 | 6 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant – normal mode, 6 = Constant – eco mode
1497 | Normal hot water temp. | °C | 6 – Write single register | S16 | 0.5 | x10 | 10 | 70 | E.g. 50°C

## Beispiel 3
Heat generator
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
Practical information: This type of control should only be used by experienced system integrators and MSR technicians.
1561 | Heat generator operation choice |  | 6 – Write single register | U16 | 1 | 0 | 0 | 8 | 0 = Heat generator off, 1 = Automatic operation, 4 = Manual heating operation, 5 = Manual cooling operation, 8 = Manual DHW operation
1562 | Manual mode setpoint temperature | °C | 6 – Write single register | U16 | 1 | x10 | 0 | 80
19484 | Manual mode output setpoint | % | 6 – Write single register | U16 | 1 | 0 | 0 | 100

## Beispiel 4
Heat generator
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
Practical information: This type of control should only be used by experienced system integrators and MSR technicians.
1561 | Heat generator operation choice |  | 6 – Write single register | U16 | 1 | 0 | 0 | 8 | 0 = Heat generator off, 1 = Automatic operation, 4 = Manual heating operation, 5 = Manual cooling operation, 8 = Manual DHW operation
1562 | Manual mode setpoint temperature | °C | 6 – Write single register | U16 | 1 | x10 | 0 | 80
19484 | Manual mode output setpoint | % | 6 – Write single register | U16 | 1 | 0 | 0 | 100

## Beispiel 5
HomeVent® comfort ventilation unit
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
23622 | Ventilation – Operation choice |  | 6 – Write single register | U16 | 1 | 0 | 0 | 5 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode
23623 | Ventilation – Normal ventilation modulation | % | 6 – Write single register | U16 | 1 | 0 | 15 | 100 | E.g. 60%
23626 | Ventilation – Humidity set value | % | 6 – Write single register | U16 | 1 | 0 | 30 | 65 | E.g. 50%

## Beispiel 6
Power limitation in line with Section 14a
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
27536 | Available el. power, dampened | kW | 6 – Write single register | S16 | 0.1 | x100 | -32700 | 32700 | E.g. 3.0 kW
27546 | Smart Grid function trigger |  | 6 – Write single register | U16 | 1 | 0 | 0 | 3 | 0 = Off, 1 = Input contacts, 2 = System bus, 3 = Available electrical power, dampened
27545 | Smart Grid via system bus |  | 6 – Write single register | U16 | 1 | 0 | 0 | 3 | 0 = Normal operation, 1 = Preferential operation, 2 = Blocked, 3 = Forced acceptance

## Beispiel 7
Heat generator/heat pump information values
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
Practical information: These data points only apply to the “newer” Hoval heat pump models, e.g. Ultra Source & Belaria Pro (WFA automatic function device), not to heat pumps with an old automatic function device (ECR), e.g. Thermalia, Belaria twin models, etc.
1477 | Heat generator – Outdoor temperature | °C | 3 – Read holding register | S16 | 0.5 | /10 | -50 | 110
18724 | Heat generator – Flow temperature setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
18725 | Heat generator – Flow temperature actual | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
1535 | Heat generator – Return temperature | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
18726 | Heat generator – Modulation | % | 3 – Read holding register | U16 | 1 | 0 | 0 | 100
18737 | Heat generator – Operating signal |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 1 | 0 = Off, 1 = On
18722 | Heat generator – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 44 | 0 = Switched off, 1 = Heating operation, 2 = Flow time heating operation, 3 = Externally blocked (also for Smart Grid eco mode), 4 = Cooling operation, 5 = Flow time cooling operation, 15 = Alarm, 16 = Fault, 17 = Blocked, 21 = WFmax switch-off, 22 = WFsetp switch-off, 26 = Bivalence deactivation, 27 = Domestic hot water charging block, 28 = Minimum off time, 29 = Minimum on time, 32 = Supplemental operation, 33 = Delay sequence H-Gen, 34 = Operation overtemperature, 42 = Manual operating mode heating, 43 = Manual operating mode hot water, 44 = Manual operating mode cooling
1561 | Heat generator – Operation choice |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 5 | 0 = Heat generator off, 1 = Automatic operation, 4 = Manual heating operation, 5 = Manual cooling operation
1516 | Heat generator – Operating hours | h | 3 – Read holding register | U32 (big endian) | 1 | 0 | 0 | 1000000
1518 | Heat generator – Switching cycles |  | 3 – Read holding register | U32 (big endian) | 1 | 0 | 0 | 1000000
25612 | Heat generator – Actual heating power | kW | 3 – Read holding register | S16 | 0.1 | 0 | 0 | 1000000
25611 | Heat generator – Actual electrical power | kW | 3 – Read holding register | S16 | 0.001 | /100 | 0 | 1000000
27490 | Heat generator – COP – Coefficient of Performance |  | 3 – Read holding register | U16 | 0.1 | /10 | 0 | 100
27467 | Heat generator – Total energy efficiency H-Gen |  | 3 – Read holding register | U16 | 0.1 | /10 | 0 | 100
31708 | Heat generator – Volume flow | l/min | 3 – Read holding register | S16 | 0.01 | /10 | 0 | 1000000
25613 | Heat generator – Total electrical energy | MWh | 3 – Read holding register | S32 (big endian) | 0.1 | /1000 | 0 | 1000000
27484 | Heat generator – Total thermal energy, heating | MWh | 3 – Read holding register | U32 (big endian) | 0.1 | /1000 | 0 | 1000000
27488 | Heat generator – Total thermal energy, domestic hot water | MWh | 3 – Read holding register | U32 (big endian) | 0.1 | /1000 | 0 | 1000000
27486 | Heat generator – Total thermal energy, cooling | MWh | 3 – Read holding register | U32 (big endian) | 0.1 | /1000 | 0 | 1000000
1534 | Heat generator – heat pump error code (WFA) |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 255 | 255 = [NO ERROR]; 74 = [W11]; 76 = [W13]; 80 = [W17]; 81 = [W18]; 82 = [W19]; 83 = [W20]; 84 = [W21]; 85 = [W22]; 86 = [W23]; 87 = [W24]; 88 = [W25]; 89 = [W26]; 90 = [W27]; 100 = [W37]; 101 = [W38]; 102 = [W39]; 103 = [W40]; 104 = [W41]; 106 = [W43]; 121 = [W58]; 122 = [W59]; 126 = [W63] |  | 128 = [B01]; 129 = [B02]; 130 = [B03]; 131 = [B04]; 132 = [B05]; 134 = [B07]; 135 = [B08]; 136 = [B09]; 137 = [B10]; 138 = [B11]; 139 = [B12]; 140 = [B13]; 142 = [B15]; 147 = [B20]; 148 = [B21]; 149 = [B22]; 150 = [B23]; 151 = [B24]; 152 = [B25]; 153 = [B26] |  |  | 159 = [B32]; 160 = [B33]; 161 = [B34]; 162 = [B35]; 163 = [B36]; 164 = [B37]; 171 = [B44]; 172 = [B45]; 173 = [B46]; 174 = [B47]; 175 = [B48]; 176 = [B49]; 177 = [B50]; 178 = [B51]; 181 = [B54]; 182 = [B55]; 183 = [B56]; 184 = [B57]; 185 = [B58] |  | 188 = [B61]; 189 = [B62]; 190 = [B63]; 192 = [E01]; 193 = [E02]; 194 = [E03]; 195 = [E04]; 198 = [E07]; 199 = [E08]; 200 = [E09]; 202 = [E11]; 203 = [E12]; 204 = [E13]; 206 = [E15]; 207 = [E16]; 213 = [E22]; 216 = [E25]; 217 = [E26]; 218 = [E27] | 219 = [E28]; 220 = [E29]; 221 = [E30]; 222 = [E31]; 230 = [E39]; 231 = [E40]; 234 = [E43]; 235 = [E44]; 236 = [E45]; 247 = [E56]; 252 = [E61]; 253 = [E62]
18723 | Heat generator – Status (WFA) |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 99 | 0 = HP off; 1 = Heating with HP; 2 = Active cooling; 3 = Block (bivalence, DHW, etc.); 4 = Domestic hot water with HP; 5 = HP frost protection; 6 = HP temperature too low | 7 = HP flow too high, 8 = Defrosting, 9 = Passive cooling, 11 = HP fault (sensor or switch), 12 = Low-pressure fault |  | 16 = Re-engage switching delay, 17 = Power supply/energy gen. block, 18 = Flow time primary, 19 = Follow-up time primary | 44 = MOP, 49 = Unsuccessful defrosting, 51 = Flow time condenser pump, 55 = Inverter fault/Modbus communication | 72 = Ground water frost protection, 73 = Flow WQ/GW circuit, 77 = Limitation compressor | 96 = Electrical power limit, 97 = Preheat compressor oil, 98 = Coldstart, 99 = Machine not configured
1513 | Heating circuit 1 – Flow temperature actual | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
19562 | Heating circuit 1 – Flow temperature setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
1501 | Heating circuit 1 – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 27 | 0 = Switched off ; 1 = Normal heating operation ; 2 = Comfort heating operation ; 3 = Economy heating operation ; 4 = Frost operation ; 5 = Forced acceptance (with force > +50%) ; 6 = Forced throttling (with force < -50%) ; 7 = Holiday operation ; 8 = Party operation ; 9 = Normal cooling operation ; 10 = Comfort cooling operation ; 11 = Economy cooling operation ; 12 = Fault ; 13 = Manual operation ; 14 = Protection cooling operation ; 15 = Party operation cooling ; 16 = Drying heating-up phase ; 17 = Drying stationary phase ; 18 = Drying cooling-down phase ; 19 = Drying end phase ; 22 = Cooling operation external/constant request ; 23 = Heating operation external/constant request ; 24 = Absent heating operation ; 25 = Absent cooling operation ; 26 = Preferential operation Smart Grid heating ; 27 = Preferential operation Smart Grid cooling ;
1478 | Heating circuit 1 – Operation choice |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 8 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode, 7 = Manual operating mode heating, 8 = Manual operating mode cooling
1493 | Heating circuit 1 – Room setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 30
19706 | Heating circuit 1 – Circulating pump status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 1 | 0 = Off, 1 = On
Practical information: Heating circuit 2 is often connected to the heating circuit expansion module for domestic hot water. This requires different Modbus data points.
1514 | Heating circuit 2 – Supply actual | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
19563 | Heating circuit 2 – Supply setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
1502 | Heating circuit 2 – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 27 | 0 = Switched off ; 1 = Normal heating operation ; 2 = Comfort heating operation ; 3 = Economy heating operation ; 4 = Frost operation ; 5 = Forced acceptance (with force > +50%) ; 6 = Forced throttling (with force < -50%) ; 7 = Holiday operation ; 8 = Party operation ; 9 = Normal cooling operation ; 10 = Comfort cooling operation ; 11 = Economy cooling operation ; 12 = Fault ; 13 = Manual operation ; 14 = Protection cooling operation ; 15 = Party operation cooling ; 16 = Drying heating-up phase ; 17 = Drying stationary phase ; 18 = Drying cooling-down phase ; 19 = Drying end phase ; 22 = Cooling operation external/constant request ; 23 = Heating operation external/constant request ; 24 = Absent heating operation ; 25 = Absent cooling operation ; 26 = Preferential operation Smart Grid heating ; 27 = Preferential operation Smart Grid cooling ;
1479 | Heating circuit 2 – Operation choice |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 8 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode, 7 = Manual operating mode heating, 8 = Manual operating mode cooling
1494 | Heating circuit 2 – Room setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
19707 | Heating circuit 2 – Circulating pump status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 1 | 0 = Off, 1 = On
Practical information: Heating circuit 3 is often connected to the heating circuit expansion module for domestic hot water. This requires different Modbus data points.
1515 | Heating circuit 3 – Supply actual | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
19564 | Heating circuit 3 – Supply setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
1503 | Heating circuit 3 – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 27 | 0 = Switched off ; 1 = Normal heating operation ; 2 = Comfort heating operation ; 3 = Economy heating operation ; 4 = Frost operation ; 5 = Forced acceptance (with force > +50%) ; 6 = Forced throttling (with force < -50%) ; 7 = Holiday operation ; 8 = Party operation ; 9 = Normal cooling operation ; 10 = Comfort cooling operation ; 11 = Economy cooling operation ; 12 = Fault ; 13 = Manual operation ; 14 = Protection cooling operation ; 15 = Party operation cooling ; 16 = Drying heating-up phase ; 17 = Drying stationary phase ; 18 = Drying cooling-down phase ; 19 = Drying end phase ; 22 = Cooling operation external/constant request ; 23 = Heating operation external/constant request ; 24 = Absent heating operation ; 25 = Absent cooling operation ; 26 = Preferential operation Smart Grid heating ; 27 = Preferential operation Smart Grid cooling ;
1480 | Heating circuit 3 – Operation choice |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 1 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode, 7 = Manual operating mode heating, 8 = Manual operating mode cooling
1495 | Heating circuit 3 – Room setpoint | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
19708 | Heating circuit 3 – Circulating pump status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 1 | 0 = Off, 1 = On
Practical information: The “SF2”/“Actual temperature bottom” temperature sensor is not always installed and therefore may report a timeout because it is not configured.
1499 | Domestic hot water – Setpoint temperature | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
1500 | Domestic hot water – Actual temperature top (SF / SF1) | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
27483 | Domestic hot water – Actual temperature bottom (SF2) | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
1504 | Domestic hot water – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 13 | 0 = Switched off ; 1 = Normal charging operation ; 2 = Comfort charging operation ; 3 = Forced throttling (with forced E < -50%) ; 4 = Forced charging (with forced E > +50%) ; 5 = Fault ; 6 = DHW draw-off (draw-off of domestic hot water active) ; 7 = Warning ; 8 = Reduced charging operation ; 9 = Frost operation ; 12 = Preferential operation Smart Grid ; 13 = Forced acceptance Smart Grid ;
1496 | Domestic hot water – Operation choice |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 5 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode
Practical information: At Hoval, there are two variants – a separate controller module (PS module -> data points in italics here) or a WPF sensor; it is not possible to have both.
27494 | Heating, cooling buffer storage tank – actual buffer temperature (WPF) | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
17386 | Heating, cooling buffer storage tank – Temperature top (PF/PF1/KPF2) | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
17387 | Heating, cooling buffer storage tank – Temperature bottom (PF2/KPF) | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
17385 | Heating, cooling buffer storage tank – Setpoint temperature | °C | 3 – Read holding register | U16 | 0.5 | /10 | 0 | 110
17384 | Heating, cooling buffer storage tank – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 9 | 0 = No request/OFF, 1 = Request, low temp., 2 = Request, charging running, 3 = Request, setpoint achieved, follow-on active, 4 = Request, setpoint achieved, 6 = Forced energy, 7 = Skimming function, 8 = Preferential operation Smart Grid, 9 = Forced acceptance Smart Grid
Comfort ventilation information values
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
Practical information: At Hoval, there are two variants – with VOC sensor and without VOC sensor. If there is no CO2 sensor, the raw values are not available (in italics).
23622 | Ventilation – Operation choice |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 5 | 0 = Standby, 1 = Week 1, 2 = Week 2, 4 = Constant, 5 = Eco mode
23625 | Ventilation – Modulation | % | 3 – Read holding register | U16 | 0.5 | 0 | 15 | 100
28942 | Ventilation – VOC extract air raw value | ppm | 3 – Read holding register | U16 | 0.5 | 0 | 0 | 10000
28943 | Ventilation – VOC outdoor air raw value | ppm | 3 – Read holding register | U16 | 0.5 | 0 | 0 | 10000
23630 | Ventilation – Air quality control |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 1 | 0 = Off, 1 = On
23631 | Ventilation – Status |  | 3 – Read holding register | U16 | 1 | 0 | 0 | 8 | 0 = Off, 1 = Normal ventilation mode, 2 = VOC mode active, 3 = Humidity mode active, 4 = Frost protection active, 5 = CoolVent active, 6 = Fault status, 7 = Summer humidity, 8 = Switch-off stop set value
23632 | Ventilation – Outside air temp. | °C | 3 – Read holding register | S16 | 0.5 | /10 | -300 | 500
23633 | Ventilation – Extract air temp. | °C | 3 – Read holding register | S16 | 0.5 | /10 | 0 | 500
23627 | Ventilation – Extract air humidity | % | 3 – Read holding register | U16 | 1 | 0 | 0 | 100

## Beispiel 8
Smart Grid activation
Register address | Data point name | Unit | Function | Type | Step width | Scaling | Minimum value | Maximum value | Possible values
27536 | Available el. power, dampened | kW | 6 – Write single register | S16 | 0.1 | x100 | -32700 | 32700 | E.g. 3.0 kW
27546 | Smart Grid function trigger |  | 6 – Write single register | U16 | 1 | 0 | 0 | 3 | 0 = Off, 1 = Input contacts, 2 = System bus, 3 = Available electrical power, dampened
27545 | Smart Grid via system bus |  | 6 – Write single register | U16 | 1 | 0 | 0 | 3 | 0 = Normal operation, 1 = Preferential operation, 2 = Blocked, 3 = Forced acceptance
27528 | Smart Grid room setpoint offset heating heating circuit 1 | K (°C) | 6 – Write single register | S16 | 0.5 | x10 | 0 | 12 | E.g. 2K
27529 | Smart Grid room setpoint offset heating heating circuit 2 | K (°C) | 6 – Write single register | S16 | 0.5 | x10 | 0 | 12 | E.g. 2K
27530 | Smart Grid room setpoint offset heating heating circuit 3 | K (°C) | 6 – Write single register | S16 | 0.5 | x10 | 0 | 12 | E.g. 2K
27509 | Smart Grid offset domestic hot water | K (°C) | 6 – Write single register | S16 | 0.5 | x10 | 0 | 30 | E.g. 10K
28839 | Smart Grid offset buffer heating | K (°C) | 6 – Write single register | S16 | 0.5 | x10 | 0 | 30 | E.g. 10K
28840 | Smart Grid offset buffer cooling | K (°C) | 6 – Write single register | S16 | 0.5 | x10 | -30 | 0 | E.g. -10K